## Instructions
NOTE: Siemens®, Simatic®, and 505® are registered trademarks of Siemens AG
VERSION 2.16 - August 8, 2011
INSTRUCTIONS:
This workbook contains two spreadsheets for use in determining CTI equivalent replacements for Simatic® 505 I/O, Rack, Power Supply products, and for calculating power budgets for CTI 2500 Series and Simatic®505 systems.
TO USE THE REPLACEMENT GUIDE:
To use the replacement guide, simply select the current Siemens® part number from the drop-down list. The system will then retrieve the following information from the database:
1. Siemens® product description,
2. The model number of the CTI exact replacement, along with it's description. Exact replacement means the module can be plugged into the rack instead of the Siemens® product with no wiring or program changes.
3. Notes for the exact replacement indicating key advantages of the CTI product over Siemens®.
4. The model of the CTI alternative replacement, along with it's description. Alternative replacement means the module can be plugged into the rack instead of the Siemens® product, but may require wiring and/or program changes to function in the application.
5. Notes for the alternative replacement indicating key advantages of the CTI product over Siemens®.
TO USE THE POWER CALCULATOR:
1. Select the base to be used in the system. Note that the CTI 2500-R16 is an exact replacement for the Siemens® 505-6516, but is lower in price.
2. Select the power supply to be used from the drop-down list. Note that the CTI 2512 and 2515 power supplies provide 50% and 100% more power, respectively, than the Siemens® supply.
3. Select the CPU or RBC to be used in this base.
4. For all the slots in the base, select the CTI or Siemens® I/O module to be installed in the slot. After each selection, the system will retrieve the module description and power usage from the database, and it will update the power used and power remaining. NOTE: The "power remaining" cell is colour coded to indicate power status. GREEN indicates there is plenty of power remaining. YELLOW is used to indicate marginal conditions where you should consider switching to a larger power supply. RED indicates the power requirement exceeds the capacity of the supply, and you must choose a higher-power supply.
5. Repeat this procedure for up to 2 remote bases in the system

## Replacement Guide
Current Siemens® Part Number | Description | List US$ | List Price US
155 | 1800KB Controller with PowerMath | #VALUE! | #VALUE!
CTI Exact Replacement Number | Description | List US$ | List Price US
2500-C400 | 3072K CPU | 0 | 0
Notes | faster, more memory, Ethernet & USB, SD card slot
Wiring Connector | not applicable
CTI Alternative Number | Description | List US$ | List Price US
none |  | 0
Notes

## Power Calculator
CTI 2500 Series and Simatic®505 PLC Power Budget Calculator
MAIN BASE
Slot | Module | Power | Description | Slots | Slots | Source | US$ List | List Price US
Base | 3 | 0 | 16-Slot Base | 16 |  | CTI | 0 | 0
Power | 3 | 75 | 120/240 VAC 75W Power Supply | 3 |  | CTI | 0 | 0
CPU | 5 | 7 | 3072K CPU | 2 |  | CTI | 0 | 0 | 16
1 | 1 | 0 | open slot | 0 | 0
2 | 1 | 0 | open slot | 0 | 0
3 | 1 | 0 | open slot | 0 | 0
4 | 1 | 0 | open slot | 0 | 0
5 | 1 | 0 | open slot | 0 | 0
6 | 1 | 0 | open slot | 0 | 0
7 | 1 | 0 | open slot | 0 | 0
8 | 1 | 0 | open slot | 0 | 0
9 | 1 | 0 | open slot | 0 | 0
10 | 1 | 0 | open slot | 0 | 0
11 | 1 | 0 | open slot | 0 | 0
12 | 1 | 0 | open slot | 0 | 0
13 | 1 | 0 | open slot | 0 | 0
14 | 1 | 0 | open slot | 0 | 0
15 | 1 | 0 | open slot | 0 | 0
16 | 1 | 0 | open slot | 0 | 0
TOTAL |  | 7 | watts |  |  |  | 0 | 0
MAXIMUM |  | 75 | watts
REMAINING |  | 68 | watts
FIRST REMOTE BASE
Slot | Module | Power | Description | Slots | Slots | Source | US$ List | List Price US
Base | 1 | 0 | not selected | 0 |  | CTI | 0 | 0
Power | 3 | 75 | 120/240 VAC 75W Power Supply | 3 |  | CTI | 0 | 0
RBC | 2 | 4 | PROFIBUS-DP RBC | 2 |  | CTI | 0 | 0
1 | 1 | 0 | PLEASE SELECT BASE TYPE | 0
2 | 1 | 0 |  | 0
3 | 1 | 0 |  | 0
4 | 1 | 0 |  | 0
5 | 1 | 0 |  | 0
6 | 1 | 0 |  | 0
7 | 1 | 0 |  | 0
8 | 1 | 0 |  | 0
9 | 1 | 0 |  | 0
10 | 1 | 0 |  | 0
11 | 1 | 0 |  | 0
12 | 1 | 0 |  | 0
13 | 1 | 0 |  | 0
14 | 1 | 0 |  | 0
15 | 1 | 0 |  | 0
16 | 1 | 0 |  | 0
TOTAL |  | 4 | watts |  |  |  | 0 | 0
MAXIMUM |  | 75 | watts
REMAINING |  | 71 | watts
SECOND REMOTE BASE
Slot | Module | Power | Description | Slots | Slots | Source | US$ List | List Price US
Base | 1 | 0 | not selected | 0 |  | CTI | 0 | 0
Power | 3 | 75 | 120/240 VAC 75W Power Supply | 3 |  | CTI | 0 | 0
RBC | 2 | 4 | PROFIBUS-DP RBC | 2 |  | CTI | 0 | 0
1 | 1 | 0 | PLEASE SELECT BASE TYPE | 0
2 | 1 | 0 |  | 0
3 | 1 | 0 |  | 0
4 | 1 | 0 |  | 0
5 | 1 | 0 |  | 0
6 | 1 | 0 |  | 0
7 | 1 | 0 |  | 0
8 | 1 | 0 |  | 0
9 | 1 | 0 |  | 0
10 | 1 | 0 |  | 0
11 | 1 | 0 |  | 0
12 | 1 | 0 |  | 0
13 | 1 | 0 |  | 0
14 | 1 | 0 |  | 0
15 | 1 | 0 |  | 0
16 | 1 | 0 |  | 0
TOTAL |  | 4 | watts |  |  |  | 0 | 0
MAXIMUM |  | 75 | watts
REMAINING |  | 71 | watts
THIRD REMOTE BASE
Slot | Module | Power | Description | Slots | Slots | Source | US$ List | List Price US
Rack | 3 | 0 | 16-Slot Base | 16 |  | CTI | 0 | 0
Power | 3 | 75 | 120/240 VAC 75W Power Supply | 3 |  | CTI | 0 | 0
RBC | 2 | 4 | PROFIBUS-DP RBC | 2 |  | CTI | 0 | 0
1 | 1 | 0 | open slot | 0 | 0
2 | 1 | 0 | open slot | 0 | 0
3 | 1 | 0 | open slot | 0 | 0
4 | 1 | 0 | open slot | 0 | 0
5 | 1 | 0 | open slot | 0 | 0
6 | 1 | 0 | open slot | 0 | 0
7 | 1 | 0 | open slot | 0 | 0
8 | 1 | 0 | open slot | 0 | 0
9 | 1 | 0 | open slot | 0 | 0
10 | 1 | 0 | open slot | 0 | 0
11 | 1 | 0 | open slot | 0 | 0
12 | 1 | 0 | open slot | 0 | 0
13 | 1 | 0 | open slot | 0 | 0
14 | 1 | 0 | open slot | 0 | 0
15 | 1 | 0 | open slot | 0 | 0
16 | 1 | 0 | open slot | 0 | 0
TOTAL |  | 4 | watts |  |  |  | 0 | 0
MAXIMUM |  | 75 | watts
REMAINING |  | 71 | watts
Total System Price | [6 empty] | 0

## Rev History (hidden)
Revision History
Date | Version | Comments
2002-10-17 | 1 | Changed 2589 to 2589-A
Removed 16/32 login capability from 2597 and 2599
2003-01-10 | 1.1 | moved 2589-A from exact to alternative replacement for 4116, 4132
2003-01-14 | X | Grantek enhancements (Ranjan Acharya)
2003-02-06 | 1.2 | Changed back to CTI, added 2572-A, 2500-R16, 2505-VSIM, 2559-RTD, fixed lots in problems in exact and alternate replacement notes
2003-03-10 | 1.3 | Changed price on 2560-A from $1900 to $1950
2003-04-15 | 1.4 | Added 2588-8, 2596-8, 2598-8
2003-05-07 | 1.5 | Added trademark to Siemens and Simatic
2003-11-06 | 1.6 | Update Siemens prices, added new CTI products
2004-01-20 | 1.7 | Added 2500-RBC selection on remote bases, added 3rd remote base
2004-03-24 | 1.8 | Changed 505-2571 cross to 2573-MOD
2004-09-01 | 1.9 | Updated CTI prices
added 2577
2005-01-10 | 2 | Added 2500-R4, CPUs, 485 RBC, 2502, updated Siemens prices
2005-02-15 | 2.1 | Added 2500-SSB, changed price on 2500-R4
2005-09-01 | 2.2 | Changed 2500-R4, 2559-RTD status, updated CTI prices
2006-12-19 | 2.3 | Added obsolete Siemens processors
2007-01-24 | 2.4 | Added 2513, noted incompatibility with 2512,2515 on 505-6511
2008-01-02 | 2.5 | Added scaling note on 2501
2008-02-08 | 2.6 | Added 2500-R11-A
2008-07-11 | 2.7 | Added note for Profibus annex card on 545-1103, 545-1105
2008-09-08 | 2.8 | Removed "in development" from 2502 and CPUs, updated RIO to RIO-A
2009-01-20 | 2.9 | Added Series 500 modules
2009-07-07 | 2.1 | Added 520, 525, 530, 535, 560, 575 processors, fixed 4916-A
2009-09-24 | 2.11 | Added 500-2151, 500-2151-A power supplies
2010-05-18 | 2.12 | Added 2500-C300 + memory expansion note on 545-1101
2010-08-09 | 2.13 | Added I/O connector 2500-40F
2010-11-18 | 2.14 | Added 2512-A and 2589-B
2011-04-26 | 2.15 | Added Note on 505-6660-A
2011-08-08 | 2.16 | Updates

## Data (hidden)
505 Product Database
Model | Description | Power (W) | Slots | List Price (US$) | Source | Connector | CTI Exact Replacement | CTI Alternative | Exact Notes | Alternative Notes | Catalogue Number | Ontor Grantek Price ($CA)
Racks
** not configured | not selected | 0 | 0 | 0 | CTI
2500-R11-A | 11-Slot Redundant base | 0 | 11 | 0 | CTI
2500-R16-A | 16-Slot Base | 0 | 16 | 0 | CTI
2500-R4 | 4-Slot Base | 0 | 4 | 0 | CTI
2500-R8 | 8-Slot Base | 0 | 8 | 0 | CTI
505-6504 | 4-Slot Base | 0 | 4 | 0 | Siemens® |  | 2500-R4 |  | exact replacement |  | PPX:505-6504 | 0
505-6508 | 8-Slot Base | 0 | 8 | 0 | Siemens® |  | 2500-R8 |  | exact replacement |  | PPX:505-6508 | 0
505-6511 | 11-Slot Base (redundant) | 0 | 11 | 0 | Siemens® |  | 2500-R11-A |  | exact replacement |  | PPX:505-6511 | 0
505-6516 | 16-Slot Base | 0 | 16 | 0 | Siemens® |  | 2500-R16-A |  | exact replacement |  | PPX:505-6516 | 0
Power Supplies
** not configured | open
2510 | 125VDC 60W Power Supply | 55 | 3 | 0 | CTI
2512 | 120/240 VAC 75W Power Supply | 75 | 3 | 0 | CTI
2513 | 24VDC 75W Power Supply | 75 | 3 | 0 | CTI
2515 | 120/240VAC 100W Power Supply | 100 | 3 | 0 | CTI
505-6660 | 110/220 VAC 55W Power Supply | 55 | 3 | 0 | Siemens® |  | 2512 | 2515 |  |  | PPX:505-6660 | 0
505-6663-A | 24 VDC 55W Power Supply | 55 | 3 | 0 | Siemens® | [5 empty] | PPX:505-6663-A | 0
RBC
** not configured | open
2500-RBC | PROFIBUS-DP RBC | 4 | 2 | 0 | CTI
2500-RIO-A | RS-485 RBC | 4 | 2 | 0 | CTI
505-6850-A | TI RIO (Co-axial Cable), Dual Media | 5 | 2 | Obsolete | Siemens® | [5 empty] | PPX:505-6850-A | Obsolete
505-6850-B | TI RIO (Co-axial Cable), Dual Media | 5 | 2 | Obsolete | Siemens® | [5 empty] | PPX:505-6850-B | Obsolete
505-6851-A | RS485 Remote Base Controller | 5 | 2 | Obsolete | Siemens® |  | 2500-RIO |  |  |  | PPX:505-6851-A | Obsolete
505-6851-B | RS485 Remote Base Controller | 5 | 2 | 0 | Siemens® |  | 2500-RIO |  |  |  | PPX:505-6851-B | 0
505-6870 | PROFIBUS-DP | 5 | 2 | 0 | Siemens® |  | 2500-RBC |  |  |  | PPX:505-6870 | 0
CPU
** not configured | open
2500-C100 | 128K CPU | 7 | 2 | 0 | CTI
2500-C200 | 256K CPU | 7 | 2 | 0 | CTI
2500-C300 | 512K CPU | 7 | 2 | 0 | CTI
2500-C400 | 3072K CPU | 7 | 2 | 0 | CTI
545-1101 | 192KB Controller | 8.5 | 2 | Obsolete | Siemens®
545-1102 | 192KB Controller | 8.5 | 2 | Obsolete | Siemens®
545-1103 | 96KB Controller | 8.5 | 2 | Obsolete | Siemens®
545-1104 | 192KB Controller | 8.5 | 2 | Obsolete | Siemens®
545-1105 | 96KB Controller | 8.5 | 2 | 0 | Siemens®
545-1106 | 192KB Controller | 8.5 | 2 | 0 | Siemens®
555-1101 | 384KB Controller | 8.5 | 2 | Obsolete | Siemens®
555-1102 | 1920KB Controller | 8.5 | 2 | Obsolete | Siemens®
555-1103 | 384KB Controller | 8.5 | 2 | Obsolete | Siemens®
555-1104 | 1920KB Controller | 8.5 | 2 | Obsolete | Siemens®
555-1105 | 384KB Controller with PowerMath | 8.5 | 2 | 0 | Siemens®
555-1106 | 1800KB Controller with PowerMath | 8.5 | 2 | 0 | Siemens® |  | 2500-C400 |  |  |  | PPX:555-1106 | 0
I/O Modules
** not configured | open slot
2500-C100 | 128K CPU | 7 | 2 | 0 | CTI | not applicable
2500-C200 | 256K CPU | 7 | 2 | 0 | CTI | not applicable
2500-C300 | 512K CPU | 7 | 2 | 0 | CTI | not applicable
2500-C400 | 3072K CPU | 7 | 2 | 0 | CTI | not applicable
2500-R11-A | 11-Slot Redundant Base | 0 | 11 | 0 | CTI | not applicable
2500-R16-A | 16-Slot Base | 0 | 16 | 0 | CTI | not applicable
2500-R4 | 4-Slot Base | 0 | 4 | 0 | CTI | not applicable
2500-R8 | 8-Slot Base | 0 | 8 | 0 | CTI | not applicable
2500-RBC | PROFIBUS-DP RBC | 4 | 2 | 0 | CTI | not applicable
2500-RIO-A | RS-485 RBC | 4 | 2 | 0 | CTI | not applicable
2500-SSB | Blank Bezel | 0 | 1 | 0 | CTI | not applicable
2501 | 8pt Analog Input / 4pt Analog Output | 5 | 1 | 0 | CTI | 2500-40F
2502 | High Speed Encoder-Counter Module | 5 | 1 | 0 | CTI | 2500-40F
2505 | Vibration Sensor Interface Module | 10 | 2 | 0 | CTI | included
2507 | Virbration Monitoring Module (in development) | 10 | 2 | 0 | CTI | not applicable |  |  | in development
2512 | 120/240 VAC 75W Power Supply | 0 | 3 | 0 | CTI | included
2512-A | 120/240 VAC 75W Power Supply | 0 | 3 | 0 | CTI | included
2513 | 24VDC 75W Power Supply | 75 | 3 | 0 | CTI | included
2515 | 120/240VAC 100W Power Supply | 0 | 3 | 0 | CTI | included
2530 | 8pt Form-C 6A Relay Output | 1 | 1 | 0 | CTI | 2500-40F
2531 | 32pt Form-A 4A Relay Output | 2 | 1 | 0 | CTI | 2500-40F
2532 | 16pt Form-A 4A Relay Output | 2 | 1 | 0 | CTI | 2500-40F
2534 | 8pt Form-C 4A Relay Output | 1 | 1 | 0 | CTI | 2500-40F
2541 | Warm Back-up Module | 6 | 2 | 0 | CTI | included
2550-A | 8pt Isolated Analog Input | 6 | 1 | 0 | CTI | 2500-40F
2551-A | 8pt Isolated Thermocouple Input | 2.4 | 1 | 0 | CTI | included
2552-A | 8pt Isolated RTD Input | 2.8 | 1 | 0 | CTI | included
2553-A | MAG Meter Input Module | 2.5 | 1 | 0 | CTI | 2500-40F
2554-A | High Speed Counter Module | 2.5 | 1 | 0 | CTI | 2500-40F
2555 | 16pt Analog Input | 5 | 1 | 0 | CTI | 2500-40F
2556 | 16pt Isolated Thermocouple Input | 9 | 1 | 0 | CTI | included
2557 | 16pt Isolated RTD Input | 6 | 1 | 0 | CTI | included
2558 | 8pt Analog Input | 3 | 1 | 0 | CTI | 2500-40F
2559-RTD | 8pt RTD Input | 3 | 1 | 0 | CTI | 2500-40F
2559-TC | 8pt Thermocouple Input | 3 | 1 | 0 | CTI | 2559-FPC
2560-A | 8pt Isolated Analog Output | 2 | 1 | 0 | CTI | 2500-40F
2562 | 8pt Analog Output | 1.7 | 1 | 0 | CTI | 2500-40F
2564-A | Pulse Output | 2 | 1 | 0 | CTI |  |  |  | mature
2571 | Program Port Expander | 5 | 1 | 0 | CTI | not applicable |  |  | replaced by 2573-MOD
2572 | Ethernet TCP/IP Adapter | 6 | 1 | 0 | CTI | not applicable
2572-A | Fast Ethernet TCP/IP Adapter (100Mbit) | 5 | 1 | 0 | CTI | not applicable | 2572 |  | Enhanced version of 2572, with 100Mbit support, other new features
2573-MOD | Serial Interface Adapter | 6 | 1 | 0 | CTI | not applicable
2573-TCM2 | Serial Interface Adapter | 6 | 1 | 0 | CTI | not applicable |  |  | replaced by 2573-MOD
2576 | DeviceNet Scanner | 7 | 2 | 0 | CTI | included
2577 | Profibus Slave Adapter | 6 | 1 | 0 | CTI | not applicable
2580 | 16pt 120VAC Isolated Input | 1 | 1 | 0 | CTI | 2500-40F
2581 | 16pt 24VDC Isolated Input | 1 | 1 | 0 | CTI | 2500-40F
2582 | 16pt 125VDC Isolated Input | 1 | 1 | 0 | CTI | 2500-40F
2585 | 16pt TTL Input | 1.4 | 1 | 0 | CTI | included
2588-8 | 8pt Universal Input | 1.5 | 1 | 0 | CTI | 2500-40F
2589-A / 2589-B | 8/16/32pt Universal Input | 1.8 | 1 | 0 | CTI | 2500-40F
2590-A | 16pt 120VAC 2A Isolated Output | 1 | 1 | 0 | CTI | 2500-40F
2590-EF | 16pt 120VAC 2A Isolated Output, Front Panel Fuses | 2.4 | 2 | 0 | CTI | 2500-40F
2591-A | 16pt 24VDC 2A Isolated Output | 1 | 1 | 0 | CTI | 2500-40F
2591-EF | 16pt 24VDC 2A Isolated Output, Front Panel Fuses | 2.4 | 2 | 0 | CTI | 2500-40F
2595 | 16pt TTL Output | 2 | 1 | 0 | CTI | included
2596 | 16pt 11-125VDC 2A Output | 1.1 | 1 | 0 | CTI | 2500-40F
2596-8 | 8pt 11-125VDC 2A Output | 1.1 | 1 | 0 | CTI | 2500-40F
2597 | 32pt 11-125VDC 2A Output | 1.1 | 1 | 0 | CTI | 2500-40F
2598 | 16pt 11-240VAC 2A Output | 1.1 | 1 | 0 | CTI | 2500-40F
2598-8 | 8pt 11-240VAC 2A Output | 1.1 | 1 | 0 | CTI | 2500-40F
2599 | 32pt 11-240VAC 2A Output | 1.1 | 1 | 0 | CTI | 2500-40F
500-2151 | 110/220 VAC Power Supply |  |  |  | Siemens® |  | 2512 | 2515 | 2500-PADP and rewiring needed | 2500-PADP and rewiring needed
500-2151A | 110/220 VAC Power Supply |  |  |  | Siemens® |  | 2512 | 2515 | 2500-PADP and rewiring needed | 2500-PADP and rewiring needed
500-5001 | 110VAC 8pt Input |  |  |  | Siemens® |  | 2588-8 | 2589-A / 2589-B | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5002 | 240VAC 8pt Input |  |  |  | Siemens® |  | 2588-8 | 2589-A / 2589-B | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5005 | 24VDC 8pt Input |  |  |  | Siemens® |  | 2588-8 | 2589-A / 2589-B | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5006 | 48VDC 8pt Input |  |  |  | Siemens® |  | 2588-8 | 2589-A / 2589-B | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5007 | TTL 8pt Input |  |  |  | Siemens® |  | 2585 | none | 2500-IADP and rewiring needed, more points on 2585
500-5008 | 24VDC 8pt Input |  |  |  | Siemens® |  | 2588-8 | 2589-A / 2589-B | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5009 | Analog 4pt Input |  |  |  | Siemens® |  | 2558 | 2550-A | 2500-IADP and rewiring needed, more points on 2558 | 2500-IADP and rewiring needed, isolated module
500-5010 | 24/48 VAC 8pt Output |  |  |  | Siemens® |  | 2598-8 | 2599 | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5011 | 110VAC 8pt Output |  |  |  | Siemens® |  | 2598-8 | 2599 | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5012 | 240VAC 8pt Output |  |  |  | Siemens® |  | 2598-8 | 2599 | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5013 | 24/48VDC 8pt Output |  |  |  | Siemens® |  | 2596-8 | 2597 | 2500-IADP and rewiring needed | 32pt module, 2500-IADP and rewiring needed
500-5016 | Analog 2pt Output |  |  |  | Siemens® |  | 2562 | 2560-A | 2500-IADP and rewiring needed, more points on 2562 | 2500-IADP and rewiring needed, isolated module
500-5018 | Word 8pt Input |  |  |  | Siemens® |  | none | 2585 |  | 1 word input, 2500-IADP and rewiring needed
500-5019 | Word 8pt Output |  |  |  | Siemens® |  | none | 2595 |  | 1 word output, 2500-IADP and rewiring needed
500-5030 | 24VDC 32pt Input |  |  |  | Siemens® |  | 2589-A / 2589-B | none | 2500-IADP and rewiring needed
500-5031 | 24VDC 32pt Output |  |  |  | Siemens® |  | 2597 | none | 2500-IADP and rewiring needed
500-5032 | 110VAC 6pt Isolated Input |  |  |  | Siemens® |  | 2580 | none | 2500-IADP and rewiring needed
500-5033 | 110VAC 4pt Isolated Output |  |  |  | Siemens® |  | 2590-A | none | 2500-IADP and rewiring needed
500-5037A | Analog 8pt Input |  |  |  | Siemens® |  | 2558 | 2550-A | 2500-IADP and rewiring needed | 2500-IADP and rewiring needed, isolated module
500-5047A | Analog 8pt Output |  |  |  | Siemens® |  | 2562 | 2560-A | 2500-IADP and rewiring needed | 2500-IADP and rewiring needed, isolated module
500-5048 | 24VDC 6pt Isolated Input |  |  |  | Siemens® |  | 2581 | none | 2500-IADP and rewiring needed
500-5049 | 24VDC 4pt Isolated Output |  |  |  | Siemens® |  | 2591-A | none | 2500-IADP and rewiring needed
500-5051 | 8pt Thermocouple Input |  |  |  | Siemens® |  | 2559-TC | none | 2500-IADP and rewiring needed
500-5052 | 16pt RTD Input |  |  |  | Siemens® |  | 2557 | none | 2500-IADP and rewiring needed
500-5055 | 110VAC 32pt Input |  |  |  | Siemens® |  | 2589-A / 2589-B | none | 2500-IADP and rewiring needed
500-5056 | 24/110VAC 32pt Output |  |  |  | Siemens® |  | 2599 | none | 2500-IADP and rewiring needed
500-5061 | 8pt Relay |  |  |  | Siemens® |  | 2534 | 2530 | 2500-IADP and rewiring needed | 6A current
500-5062 | 8pt Relay |  |  |  | Siemens® |  | 2534 | 2530 | 2500-IADP and rewiring needed | 6A current
500-5187 | 16pt 110VDC input |  |  |  | Siemens® |  | 2589-A / 2589-B | none | 2500-IADP and rewiring needed
500-5192 | 32pt 48VDC input |  |  |  | Siemens® |  | 2589-A / 2589-B | none | 2500-IADP and rewiring needed
500-5194 | 32pt TTL input |  |  |  | Siemens® |  | 2585 | none | 2500-IADP and rewiring needed, note 2585 has only 16pt
505-2555 | 16pt Differential Analog Input | 5 | 1 | 0 | CTI |  | 2555-A | 2550-A | CTI Identical Product | 8pt, isolated per channel, different connector wiring
505-2556 | 16pt Isolated Thermocouple Input | 9 | 1 | 0 | CTI |  | 2556 | 2551-A | CTI Identical Product | 8pt, isolated per channel, different connector wiring
505-2557 | 16pt Isolated RTD Input | 6 | 1 | 0 | CTI |  | 2557 | 2552-A | CTI Identical Product | 8pt, isolated per channel, different connector wiring
505-2571 | Program Port Expander | 5 | 1 | 0 | CTI |  | 2573-MOD | none | Not 100% compatible
505-2580 | 16pt 120VAC Isolated Input | 1 | 1 | 0 | CTI |  | 2580 | 2589-A / 2589-B | CTI Identical Product | 32pt, isolated in groups of 4 or 8, wider operating voltage, different connector wiring
505-2590-A | 16pt 120VAC 2A Isolated Output | 1 | 1 | 0 | CTI |  | 2590-A | 2599 | CTI Identical Product | 32pt, isolated in groups of 4 or 8, wider operating voltage, different connector wiring
505-3508 | 8pt 24VDC 0.5A Output | 2.5 | 1 | Obsolete | Siemens® |  | none | 2596 | contact CTI for special quote | 16pt, sourcing, 2A output, wider voltage range, individually fused outputs | PPX:505-3508 | Obsolete
505-3516 | 16pt 24VDC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | none | 2596 |  | sourcing, 2A output, wider voltage range, individually fused outputs | PPX:505-3516 | Obsolete
505-3532 | 32pt 24VDC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | none | 2597 |  | 32pt, sourcing, isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs | PPX:505-3532 | Obsolete
505-3708 | 8pt 24VDC 2A Output | 5 | 2 | 0 | Siemens® |  | none | 2596 | contact CTI for special quote | 16pt, sourcing, single wide, 2A output, wider voltage range, individually fused outputs | PPX:505-3708 | Obsolete
505-3716 | 16pt 24VDC 2A Output | 5 | 2 | 0 | Siemens® |  | none | 2596 |  | sourcing, single wide, 2A output, wider voltage range, individually fused outputs | PPX:505-3716 | Obsolete
505-3732 | 32pt 24VDC 2A Output | 5 | 2 | 0 | Siemens® |  | none | 2597 |  | 32pt, sourcing, isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs | PPX:505-3732 | Obsolete
505-4008-A | 8pt 24VAC Input | 2 | 1 | 0 | Siemens® |  | 2588-8 | 2589-A / 2589-B | wider voltage range | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login | PPX:505-4008-A | Obsolete
505-4016-A | 16pt 24VAC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4016-A | Obsolete
505-4032-A | 32pt 24VAC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4032-A | 0
505-4108 | 8pt 12VDC Input | 2 | 1 | 0 | Siemens® |  | none | 2588-8 | contact CTI for special quote |  | PPX:505-4108 | Obsolete
505-4116 | 16pt 12VDC Input | 2 | 1 | 0 | Siemens® |  | none | 2589-A / 2589-B |  | exact replacement for 505-4116 used at 12VDC | PPX:505-4116 | Obsolete
505-4132 | 32pt 12VDC Input | 2 | 1 | 0 | Siemens® |  | none | 2589-A / 2589-B |  | exact replacement for 505-4132 used at 12VDC | PPX:505-4132 | Obsolete
505-4208-A | 8pt 120VAC Input | 2 | 1 | 0 | Siemens® |  | 2588-8 | 2589-A / 2589-B | wider voltage range | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login | PPX:505-4208-A | 0
505-4216-A | 16pt 120VAC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4216-A | 0
505-4232-A | 32pt 120VAC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4232-A | 0
505-4308 | 8pt 24VDC Input | 2 | 1 | Obsolete | Siemens® |  | 2588-8 | 2589-A / 2589-B | wider voltage range | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login | PPX:505-4308 | 0
505-4316-A | 16pt 24VDC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4316-A | 0
505-4317 | 24VDC Isolate/Interrupt Module | 2 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-4317 | Obsolete
505-4318 | 48VDC Isolate/Interrupt Module | 2 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-4318 | Obsolete
505-4319 | 125VDC Isolate/Interrupt Module | 2 | 1 | Obsolete | Siemens® |  | none | none |  |  | PPX:505-4319 | Obsolete
505-4320 | 30VDC Isolate/Interrupt Module | 2 | 1 | Obsolete | Siemens® |  | none | none |  |  | PPX:505-4320 | 0
505-4332 | 32pt 24VDC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4332 | 0
505-4408-A | 8pt 240VAC Input | 2 | 1 | 0 | Siemens® |  | 2588-8 | 2589-A / 2589-B | wider voltage range | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login | PPX:505-4408-A | Obsolete
505-4416-A | 16pt 240VAC Input | 2 | 1 | 0 | Siemens® |  | 2589-A / 2589-B | none | 32pt, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4416-A | 0
505-4432-A | 32pt 240VAC Input | 2 | 2 | 0 | Siemens® |  | 2589-A / 2589-B | none | single-wide, isolated in groups of 4 or 8, wider voltage range, configurable for 16pt or 32pt base login |  | PPX:505-4432-A | 0
505-4508 | 8pt 24VDC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | 2596-8 | 2596 | 2A output, wider voltage range, individually fused outputs | 16pt, 2A output, wider voltage range, individually fused outputs | PPX:505-4508 | Obsolete
505-4516 | 16pt 24VDC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | 2596 | 2597 | 2A output, wider voltage range, individually fused outputs | 32pt, isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs | PPX:505-4516 | 0
505-4532 | 32pt 24VDC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | 2597 | none | isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs |  | PPX:505-4532 | 0
505-4608 | 8pt 120VAC 0.5A Output | 2.5 | 1 | Obsolete | Siemens® |  | 2598-8 | 2598 | 2A output, wider voltage range, individually fused outputs | 16pt, 2A output, wider voltage range, individually fused outputs | PPX:505-4608 | 0
505-4616 | 16pt 120VAC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | 2598 | 2599 | 2A output, wider voltage range, individually fused outputs | 32pt, isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs | PPX:505-4616 | 0
505-4632 | 32pt 120VAC 0.5A Output | 2.5 | 1 | 0 | Siemens® |  | 2599 | none | isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs |  | PPX:505-4632 | 0
505-4708 | 8pt 24VDC 2A Output | 5 | 2 | 0 | Siemens® |  | 2596-8 | 2596 | 2A output, wider voltage range, individually fused outputs | 16pt, single wide, isolated in group of 4 or 8, wider voltage range, individually fused outputs | PPX:505-4708 | Obsolete
505-4716 | 16pt 24VDC 2A Output | 5 | 2 | 0 | Siemens® |  | 2596 | 2597 | single wide, wider voltage range, individually fused outputs | 32pt, single wide, isolated in groups of 4 or 8, 2A output, wider voltage range, individually fused outputs | PPX:505-4716 | 0
505-4732 | 32pt 24VDC 2A Output | 5 | 2 | 0 | Siemens® |  | 2597 | none | single wide, isolated in groups of 4 or 8, wider voltage range, individually fused outputs |  | PPX:505-4732 | 0
505-4808 | 8pt 120VAC 2A Output | 5 | 2 | Obsolete | Siemens® |  | 2598-8 | 2598 | 2A output, wider voltage range, individually fused outputs | 16pt,single wide, isolated in groups of 4 or 8, wider voltage range, individually fused outputs | PPX:505-4808 | 0
505-4816 | 16pt 120VAC 2A Output | 5 | 2 | 0 | Siemens® |  | 2598 | 2599 | single wide, wider voltage range, individually fused outputs | 32pt, single wide, isolated in groups of 4 or 8, wider voltage range, individually fused outputs | PPX:505-4816 | 0
505-4832 | 32pt 120VAC 2A Output | 5 | 2 | 0 | Siemens® |  | 2599 | none | single wide, isolated in groups of 4 or 8, wider voltage range, individually fused outputs |  | PPX:505-4832 | 0
505-4908 | 8pt Form-C 2A Relay Output | 2.5 | 1 | 0 | Siemens® |  | 2534 | 2532 | twice the current on outputs, up to 10 times longer contact life, individually fused outputs | twice the current on outputs, 16 Form-A relays, up to 10 times longer contact life, individually fused outputs | PPX:505-4908 | 0
505-4916-A | 16pt Form-A 2A Relay Output | 2.5 | 1 | 0 | Siemens® |  | 2532 | 2531 | twice the current on outputs, up to 10 times longer contact life, individually fused outputs | twice the current on outputs, 32 Form-A relays, up to 10 times longer contact life, individually fused outputs, needs rewiring to replace 505-4916-A | PPX:505-4916-A | 0
505-4932-A | 32pt Form-A 2A Relay Output | 2.5 | 2 | 0 | Siemens® |  | 2531 | none | twice the current on outputs, up to 10 times longer contact life, individually fused outputs |  | PPX:505-4932-A | 0
505-5100 | Turbo Plastic Module | 7 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-5100 | 0
505-5103 | Turbo Parison Module | 7 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-5103 | 0
505-5184 | Modbus NIM | 8 | 1 | 0 | Siemens® |  | none | 2573-MOD |  | Minimal changes required. See application note onb www.controltechnology.com: Guide to Replacing 505-5184 using CTI 2573-MOD. | PPX:505-5184 | 0
505-5190 | 6MT Adapter | 4 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-5190 | 0
505-5417 | 16pt Form-C 1A Relay Output | 3 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-5417 | 0
505-5518 | 16pt Form-C 1A Relay Output w/snubbers | 2 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-5518 | 0
505-6010 | Input Simulator | 2 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-6010 | Obsolete
505-6011 | Output Simulator | 2.5 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-6011 | Obsolete
505-6108-A | 8pt Analog Input | 4 | 1 | Obsolete | Siemens® |  | 2558 | 2550-A | better isolation, more speed, better accuracy, better resolution, less backplane power | isolation per channel, better accuracy | PPX:505-6108-A | Obsolete
505-6108-B | 8pt Analog Input | 4 | 1 | 0 | Siemens® |  | 2558 | 2550-A | better isolation, more speed, better resolution, less backplane power | isolation per channel, better accuracy | PPX:505-6108-B | 0
505-6208-A | 8pt Analog Output | 2 | 1 | 0 | Siemens® |  | 2562 | 2560-A | better accuracy, more speed, less backplane power | isolation per channel, better accuracy | PPX:505-6208-A | Obsolete
505-6208-B | 8pt Analog Output | 2 | 1 | 0 | Siemens® |  | 2562 | 2560-A | better accuracy, more speed, less backplane power | isolation per channel, better accuracy | PPX:505-6208-B | 0
505-6308 | 8pt Word Input | 4 | 2 | Obsolete | Siemens® |  | none | 2585 |  | 16pt, different wiring | PPX:505-6308 | 0
505-6408 | 8pt Word Output | 5 | 2 | Obsolete | Siemens® |  | none | 2595 |  | 16pt, different wiring | PPX:505-6408 | 0
505-6504 | 4-Slot Base | 0 | 4 | 0 | Siemens® |  | 2500-R4 | none | Exact replacement
505-6508 | 8-Slot Base | 0 | 8 | 0 | Siemens® |  | 2500-R8 | none | Exact replacement
505-6511 | 11-Slot Base | 0 | 11 | 0 | Siemens® |  | 2500-R11-A | none | Exact replacement
505-6516 | 16-Slot Base | 0 | 16 | 0 | Siemens® |  | 2500-R16-A | none | Exact replacement
505-6660 | 110/220 VAC 55W Power Supply | 0 | 3 | 0 | Siemens® |  | 2512 | 2515 | 50% more power, better resistance to brown-outs, use 2512-A when using redundant base | twice the power, better resistance to brown-outs, use 2512-A when using redundant base | PPX:505-6660 | 0
505-6660-A | 110/220 VAC 55W Power Supply | 0 | 3 | 0 | Siemens® |  | 2512-A | 2515 | 50% more power, better resistance to brown-outs, can use 2512 if redundancy not required | twice the power, better resistance to brown-outs, use 2512-A when using redundant base | PPX:505-6660-A | Obsolete
505-6660-B | 110/220 VAC 55W Power Supply | 0 | 3 | 0 | Siemens® |  | 2512-A | 2515 | 50% more power, better resistance to brown-outs, can use 2512 if redundancy not required | twice the power, better resistance to brown-outs, use 2512-A when using redundant base | PPX:505-6660-B | 0
505-6663 | 24VDC 55W Power Supply | 0 | 3 | 0 | Siemens® |  | 2513 | none | 50% more power, better resistance to brown-outs
505-6851-A | RS485 Remote Base Controller | 5 | 2 | Obsolete | Siemens® |  | 2500-RIO-A | none
505-6851-B | RS485 Remote Base Controller | 5 | 2 | 0 | Siemens® |  | 2500-RIO-A | none
505-6860 | RS485 to COAX Converter | 5 | 2 | 0 | Siemens® |  | none | none
505-6870 | PROFIBUS-DP RBC | 5 | 2 | 0 | Siemens® |  | 2500-RBC | none | Exact replacement
505-7002 | High Speed Counter / Encoder Module | 3.5 | 1 | 0 | Siemens® |  | 2502 | 2554-A |  |  | PPX:505-7002 | 0
505-7003 | High Speed Counter / Encoder Module | 2.5 | 1 | 0 | Siemens® |  | none | 2554-A |  |  | PPX:505-7003 | 0
505-7012 | 8in/4out Analog | 3.5 | 1 | 0 | Siemens® |  | 2501 | none | better isolation, more speed, better accuracy, NOTE: 505-7012 scaling is not supported on 2501 |  | PPX:505-7012 | 0
505-7012-A | 8in/4out Analog | 3.5 | 1 | 0 | Siemens® |  | 2501 | none | better isolation, more speed, better accuracy, NOTE: 505-7012-A scaling is not supported on 2501
505-7016 | 8in/4out Analog | 3.5 | 1 | 0 | Siemens® |  | 2501 | none | better isolation, more speed, better accuracy, NOTE: 505-7016 scaling is not supported on 2501 |  | PPX:505-7016 | 0
505-7028 | 8pt Thermocouple Input | 2.2 | 1 | 0 | Siemens® |  | 2559-TC | 2551-A | more speed, better accuracy, individual range settings | isolation per channel, better accuracy | PPX:505-7028 | Obsolete
505-7028-A | 8pt Thermocouple Input | 2.2 | 1 | 0 | Siemens® |  | 2559-TC | 2551-A | more speed, better accuracy, individual range settings | isolation per channel, better accuracy
505-7038 | 8pt RTD Input | 2.2 | 1 | 0 | Siemens® |  | 2559-RTD | 2552-A |  | isolation per channel, better accuracy | PPX:505-7038 | 0
505-7101 | BASIC Module | 7 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-7101 | 0
505-7190 | 7MT Adapter | 5 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-7190 | Obsolete
505-7202 | Field Interface Module | 3.5 | 1 | 0 | Siemens® |  | none | none |  |  | PPX:505-7202 | 0
505-ATM-4120 | 386/ATM Module | 11 | 3 | 0 | Siemens® |  | none | none |  |  | PPX:505-ATM-4120 | Obsolete
505-CP1434-TCP | TCP/IP Module | 22 | 2 | 0 | Siemens® |  | none | 2572 |  | compatible with installed TCP/IP base, no external configuration required | PPX:505-CP1434-TCP | 0
505-CP1434-TF | H1 Module | 22 | 2 | 0 | Siemens® |  | none | 2572 |  | compatible with installed TCP/IP base, no external configuration required | PPX:505-CP1434-TF | Obsolete
505-CP2572 | Ethernet TCP/IP Adapter | 6 | 1 | 0 | Siemens® |  | 2572 | 2572-A | CTI Identical Product | Enhanced version of 2572, with 100Mbit support, other new features | PPX:505-CP2572 | Obsolete
505-CP5434-FMS | FMS Communications Processor | 5 | 1 | 0 | Siemens® |  | none | none
520-1101 | combined CPU and PSU, 1K ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-R4500, 2512 | if remote bases are present, with 2500-R4500, 2512 (also need new RBC in remote bases)
520-1102 | combined CPU and PSU, 2K ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-R4500, 2512 | if remote bases are present, with 2500-R4500, 2512 (also need new RBC in remote bases)
520-1104 | combined CPU and PSU, 4K ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-R4500, 2512 | if remote bases are present, with 2500-R4500, 2512 (also need new RBC in remote bases)
520C-1101 | CPU, 1K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
520C-1102 | CPU, 2K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
525-1101 | CPU, 1K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
525-1102 | CPU, 2K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
525-1104 | CPU, 4K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
525-1208 | CPU, 8K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
525-1212 | CPU, 12K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
530-1102 | combined CPU and PSU, 2K ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-R4500, 2512 | if remote bases are present, with 2500-R4500, 2512 (also need new RBC in remote bases)
530-1104 | combined CPU and PSU, 4K ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-R4500, 2512 | if remote bases are present, with 2500-R4500, 2512 (also need new RBC in remote bases)
530-1108 | combined CPU and PSU, 8K ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-R4500, 2512 | if remote bases are present, with 2500-R4500, 2512 (also need new RBC in remote bases)
530C-1102 | CPU, 2K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
530C-1104 | CPU, 4K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
530C-1108 | CPU, 8K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
530C-1112 | CPU, 12K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
530T-1104 | Turbo CPU, 4K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
530T-1112 | Turbo CPU, 12K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present, with 2500-RADP | if remote bases are present, with 2500-RADP (also need new RBC in remote bases)
535-1204 | CPU, 4K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
535-1208 | CPU, 8K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
535-1212 | CPU, 12K Ladder |  |  |  | Siemens® |  | 2500-C100 | 2500-C200 | if no remote bases are present | if remote bases are present (also need new RBC in remote bases)
545-1101 | 192KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C200 | 2500-C300 | faster, more memory, Ethernet & USB, SD card slot | if 545-1101 includes a memory expansion card
545-1102 | 192KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C200 | none | faster, more memory, Ethernet & USB, SD card slot
545-1103 | 96KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C100 | none | faster, more memory, Ethernet & USB, SD card slot *if Profibus-DB annex card is installed, 2500-C200 must be used
545-1104 | 192KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C200 | none | faster, more memory, Ethernet & USB, SD card slot
545-1105 | 96KB Controller | 8.5 | 2 | 0 | Siemens® |  | 2500-C100 | none | faster, more memory, Ethernet & USB, SD card slot *if Profibus-DB annex card is installed, 2500-C200 must be used
545-1106 | 192KB Controller | 8.5 | 2 | 0 | Siemens® |  | 2500-C200 | none | faster, more memory, Ethernet & USB, SD card slot
555-1101 | 384KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C300 | none | faster, more memory, Ethernet & USB, SD card slot
555-1102 | 1920KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C400 | none | faster, more memory, Ethernet & USB, SD card slot
555-1103 | 384KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C300 | none | faster, more memory, Ethernet & USB, SD card slot
555-1104 | 1920KB Controller | 8.5 | 2 | Obsolete | Siemens® |  | 2500-C400 | none | faster, more memory, Ethernet & USB, SD card slot
555-1105 | 384KB Controller with PowerMath | 8.5 | 2 | 0 | Siemens® |  | 2500-C300 | none | faster, more memory, Ethernet & USB, SD card slot
555-1106 | 1800KB Controller with PowerMath | 8.5 | 2 | 0 | Siemens® |  | 2500-C400 | none | faster, more memory, Ethernet & USB, SD card slot
560 / 565 | Discrete CPU / Special Function Card |  |  |  | Siemens® |  | 2500-C400 | 2500-C300 | depending on Program size and number of remote I/O bases (with 2500-R4 and 2512) | depending on Program size and number of remote I/O bases (with 2500-R4 and 2512)
560T / 565T | Discrete CPU / Special Function Card |  |  |  | Siemens® |  | 2500-C400 | 2500-C300 | depending on Program size and number of remote I/O bases (with 2500-R4 and 2512) | depending on Program size and number of remote I/O bases (with 2500-R4 and 2512)
575-2102 | 575 CPU |  |  |  | Siemens® |  | 2500-C400 | none | must evaluate the application
575-2103 | 575 CPU |  |  |  | Siemens® |  | 2500-C400 | none | must evaluate the application
575-2104 | 575 CPU |  |  |  | Siemens® |  | 2500-C400 | none | must evaluate the application
575-2105 | 575 CPU |  |  |  | Siemens® |  | 2500-C400 | none | must evaluate the application
575-2106 | 575 CPU |  |  |  | Siemens® |  | 2500-C400 | none | must evaluate the application |  | PPX:575-2106 | Obsolete
none
| US LIST TO LOCAL CURRENCY CONVERSION |  |  | 1

## Siemens (hidden)
Item Number | Description | Catalogue Reference | Lead Time in Days | Unit of Measurement | Item Code | List Price | Multiplier | Grantek Price
6MT14-4OCL | OUTPUT MODULE | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:2587678-8005 | TI505 BATTERY F. TI525/TI560T/TI565T CPUS AND 500-5022, 500-5035 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:2587681-8001 | EPROM 2K X 8 500 SER | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:2587681-8030 | 555 USER EEPROM | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:2587681-8036 | 505 505-7101 BASIC REL. 1.2.2 OS | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:2587693-8006 | REPLACE KEY STD | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:2587695-8038 | 505-7201 UPG.,REL 3.1 WITH MAN | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:2587705-8003 | TI505 BLANK BEZEL, 5 PCS, FOR BASE FOR TI505 PLC | ST44 | 10 | Pkg. | 89 | 0 | 100% | 0
PPX:2587705-8010 | 505 I/O SIDE ACCESS CONNECTOR | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:2587705-8011 | TI505 FRONT ACCESS CONNECTOR F. TI505 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:25897398013 | FUSE KIT, 575-6663 | ST44 | 10 | Pkg. | 89 | 0 | 100% | 0
PPX:2589739-8013 | REL 3.2 FIRMWARE UPGRADE 505-5184 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:2601094-8001 | CABLE,545/555 TISOFT, 9PF-9PF | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505/ATM-MANL-3 | USER MANUAL,505 ATM CO-PROCESSOR | ST44 | 10 |  | 89 | 0 | 100% | 0
PPX:505-4032-A | TI505 DIGITAL INPUT MODULE FOR TI505 PLC, FLOATING 32 INPUTS, 20-56V AC ENHANCED NOISE FILTER | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4208-A | TI505 DIGITAL INPUT MODULE FOR TI505 PLC, FLOATING 8 INPUTS, 79-132V AC ENHANCED NOISE FILTER | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4216-A | TI505 DIGITAL INPUT MODULE FOR TI505 PLC, FLOATING 16 INPUTS, 79-132V AC ENHANCED NOISE FILTER | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4232-A | TI505 DIGITAL INPUT MODULE FOR TI505 PLC, FLOATING 32 INPUTS, 79-132V AC ENHANCED NOISE FILTER | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-4308 | 505-4308 / 24 VDC INPUT (8 PT) | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4316-A | TI505 16 POINTS INPUT MODULE FOR TI505 48 VDC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4320 | 30VDC ISOLATE/INTERRUPT MODULE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-4332 | 505-4332 / 24 VDC INPUT (32 PT | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-4416-A | TI505 DIGITAL INPUT MODULE FOR TI505 PLC, FLOATING 16 INPUTS, 164-265V AC ENHANCED NOISE FILTER | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4432-A | TI505 DIGITAL INPUT MODULE FOR TI505 PLC, FLOATING 32 INPUTS, 164-265V AC ENHANCED NOISE FILTER FULLY REPLACING PPX:50 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4516 | 505-4516 / 0.5A DC OUT (16PT) | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-4532 | 505-4532 / 0.5A DC OUT (32PT) | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4608 | 505-4608 / 24/110 VAC OUT (8PT) | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-4616 | 505-4616 / 24/110 VAC OUT (16PT) | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4632 | 505-4632 / 24/110 VAC OUT (32PT) | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4716 | 505-4716 / 2.0A DC OUT (16PT) | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4732 | 505-4732 / 2.0A DC OUT (32PT) | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4808 | TI505 DIGITAL OUTPUT MODULE FOR TI505 PLC, FLOATING 8 OUTPUTS, 85-265V AC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4816 | TI505 DIGITAL OUTPUT MODULE FOR TI505 PLC, FLOATING 16 OUTPUTS, 85-265V AC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4832 | TI505 DIGITAL OUTPUT MODULE FOR TI505 PLC, FLOATING 32 OUTPUTS, 85-265V AC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4908 | FULLY REPLACED BY PPX:5054908A. TI505 RELAY OUTPUT MODULE FOR TI505 PLC, FLOATING 8 OUTPUTS, 220V AC/24V DC | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-4916-A | TI505 RELAY OUTPUT MODULE FOR TI505 PLC, FLOATING 16 OUTPUTS, 220 V AC / 24 V DC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-4932-A | TI505 RELAY OUTPUT MODULE FOR TI505 PLC, FLOATING 32 OUTPUTS, 220 V AC / 24 V DC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-5100 | TI505 TURBO PLASTIC MODULE FOR TI505, 5 ANALOGUE INPUTS, 4 ANALOGUE/ 4 DIGITAL OUTPUTS | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-5103 | TI505 TURBO PARISON MODULE FOR TI505, 4 DIGITAL / 5 ANALOGUE INPUTS 4 DIGITAL / 4 ANALOGUE OUTPUTS | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-5184 | TI505 NETWORK INTERFACE MODULE NIM FOR MODBUS, FOR TI505 PLC | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-5190 | TI505 INTERFACE ADAPTER FOR TI505, FOR 6MT I/O SYSTEM | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-5417 | TI505 RELAY OUTPUT MODULE FOR TI505 PLC, FLOATING 16 OUTPUTS, 115V AC/DC | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-5518 | TI505 HIGH CURRENT RELAY MODULE TI505 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6108-B | 505-6108-B,8 CHANNEL ANALOGUE INPUT | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6208-B | TI505 ANALOGUE OUTPUT MODULE FOR TI505 PLC, FLOATING, 8 OUTPUTS, 0-10V DC, 0-20 MA | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6308 | TI505 WORD INPUT MODULE FOR TI505 PLC 8 INPUTS, TTL, CMOS | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6408 | TI505 WORD OUTPUT MODULE FOR TI505 PLC 8 OUTPUTS, TTL, CMOS | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6504 | TI505 MOUNTING RACK FOR TI505 PLC 4 SLOT | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6508 | TI505 MOUNTING RACK FOR TI505 PLC 8 SLOT | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-6511 | TI505 MOUNTING RACK FOR TI505 PLC 11 SLOT, REDUNDANT | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-6516 | TI505 MOUNTING RACK FOR TI505 PLC 16 SLOT | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6660 | TI505 POWER SUPPLY MODULE F.TI505 PLC 110/220V AC, 60W | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6660-B | 505-6660B POWER SUPPLY | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6663-A | 505-6663-A/POWER SUPPLY | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6701 | 505 OPC SERVER FOR TCP/IP CARD (PPX:505-CP1434-TCP), SINGLE USER LICENCE (FLOPPY DISK). | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-6702 | 505 OPC SERVER FOR TCP/IP CARD (PPX:505-CP1434-TCP), CORPORATE LICENCE (CONTINENTAL) A LICENCE AGREEMENT HAS TO BE SIGNED | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-6851-B | 505 RBC,RS-485,DUAL MEDIA | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-6870 | TI505 L2DP REMOTE BASE CONTROLLER | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7002 | TI505 HIGH SPEED COUNTER MODULE FOR TI505 PLC 4 IN/OUTPUTS, UP TO 50KHZ | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7003 | TI505 HIGH SPEED COUNTER/ENCODER MODULE | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7012 | TI505 ANALOGUE INPUT/OUTPUT MODULE FOR TI505 PLC 8 INPUTS/4 OUTPUTS STANDARD VERSION | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7016 | TI505 ANALOGUE INPUT/OUTPUT FOR TI505 8 INPUTS/4 OUTPUTS HIGH SPEED-AUSFUEHRUNG | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:505-7028-A | 8 PT THERMOCOUPLE INPUT MODULE | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7038 | TI505 TEMPERATURE INPUT MODULE FOR TI505 PLC RTD, 8 INPUTS | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7101 | TI505 BASIC MODULE FOR TI505 PLC 28 KBYTES, BATTERY BACKED MEMORY | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7202 | TI505 FIELD INTERFACE MODULE FOR TI505 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-7339 | TI505 TIWAY NETWORK INTERFACE MODULE FOR LINKING TI505 PLC TO TIWAY 2 LOCAL LINE PORTS | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-8116-1 | USER MAN, 505-5190 6MT I/O I/F | ST44 | 10 |  | 89 | 0 | 100% | 0
PPX:505-8132-2 | USER MANUAL 505-CP2572 TCP/IP | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-CDMANUAL-2 | 505 ELECTRONIC DOCUMENTATION ON CDROM (INCLUDING OVER 50 MANUALS, SOME SOFTWARE UTILITIES AND THE ST40 CATALOGUE) | ST44 | 5 | Unit | 89 | 0 | 100% | 0
PPX:505-CP1434-TCP | TI505 TCP/IP COMMUNICATION PROCESSOR | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-CP1434TF | TI505 SINEC H1 COMMUNICATION. PROCESSOR FOR TI505 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-CP5434-DP | TI505 DP ANNEX BOARD FOR 545-1103 AND 575-2104 | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:505-CP5434-FMS | 505 PROFIBUS-FMS COM.PROCESSOR | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:545/555-8101-2 | USER MANUAL,545/555 REL3.0 SYS | ST44 | 10 |  | 99 | 0 | 100% | 0
PPX:545-1105 | 505 CPU 545-1106 WITH 192 KB MEMORY FRONT ACCESSIBLE BATTERY REPLACEMENT, USER FLASH EEPROM, INTEGRATES PROFIBUS-DP SUP | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:545-1106 | 505 CPU 545-1106 WITH 192 KB MEMORY FRONT ACCESSIBLE BATTERY REPLACEMENT, USER FLASH EEPROM, INTEGRATES PROFIBUS-DP SUP | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:555-1105 | TI505 CPU TI555, 384 KB USER MEMORY, WITH POWERMATH (TM) AND SMARTUNE (TM) FUNCTIONS. | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:555-1106 | TI505 CPU TI555, 1.8 MB USER MEMORY, WITH POWERMATH (TM) AND SMARTUNE (TM) FUNCTIONS. | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:560/65-8102 | 560/65-8102 / MAN, 560/65-8102 | ST44 | 10 |  | 89 | 0 | 100% | 0
PPX:560/65-8103-2 | USER MANUAL 560/65 HBU | ST44 | 10 |  | 89 | 0 | 100% | 0
PPX:560/65-8108 | 560/65-8108 / REDUNDANT I/O SY | ST44 | 10 |  | 89 | 0 | 100% | 0
PPX:560/65-8109 | MANUAL, 560T/565T SYSTEM | ST44 | 10 |  | 89 | 0 | 100% | 0
PPX:575-4732 | 32 PT 2.0A 24VDC OUTPUT | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SS505-6202 | SOFTSHOP PROGRAMMING SOFTWARE, SINGLE USER LICENCE REL. 3.0, 32 BIT VERSION. | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SS505-CDROM-1 | 505 SOFTSHOP REL. 3.0 CD DISK WITH COM PROFIBUS 5.0 & MANUALS (SOFTSHOP MANUAL, PROGRAMMING REFERENCE MANUAL & PROFIBUS | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SS505-UPG1 | 505 SOFTSHOP 1YR ULA IN WARRANTY | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SS505-UPG2 | TI505 SOFTSHOP ONE YEAR UPGRADE LICENCE AGREEMENT, OUT OF WARRANTY PERIOD. | ST44 | 10 | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-6202 | 505 SOFTSHOP PROGRAMMING SOFTWARE, 8 USER SITE LICENCE REL. 3.0. PLEASE APPLY FOR A SITE LICENCE AGREEMENT BEFORE PLACI | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-6230 | SOFTSHOP CORPORATE LICENCE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-6232 | 505 SOFTSHOP ADDIT.CORPORATE CDROM WITH COM PROFIBUS LICENCE & MANUALS. PLEASE PROVIDE A COPY OF YOUR ORIGINAL SOFTSHOP | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-6302 | 505 ADDITIONAL COPY 1 USER TO SOFTSHOP SITE LICENCE. PLEASE PROVIDE A COPY OF YOUR ORIGINAL SOFTSHOP SITE LICENCE AGREE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG1 | SOFTSHOP ADD 1 ULA-IN WARRANTY | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG10 | 505 SOFTSHOP 8 USER SITE LICENCE TREND/LOG UPGRADE. PLEASE PROVIDE A COPY OF YOUR ORIGINAL SOFTSHOP SITE LICENCE AGREEMENT | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG2 | TI505 SOFTSHOP SITE LICENCE ONE YEAR UPGRADE LICENCE AGREEMENT INSIDE WARRANTY PERIOD FOR ONE LICENCE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG3 | 505 SOFTSHOP 1 USER SITE LICENCE TREND/LOG UPGRADE. PLEASE PROVIDE A COPY OF YOUR ORIGINAL SOFTSHOP SITE LICENCE AGREEMENT | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG30 | TI505 SOFTSHOP CORPORATE LICENCE ONE YEAR UPGRADE LICENCE AGREEMENT. PLEASE SUPPLY A COPY OF YOUR ORI | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG32 | 505 SOFTSHOP CORPORATE LICENCE ONE YEAR UPGRADE. OUT WARRANTY PERIOD. PLEASE PROVIDE A COPY OF YOUR ORIGINAL SOFTSHOP SITE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG33 | 505 SOFTSHOP CORPORATE LICENCE ONE YEAR TREND/LOG UPGRADE. PLEASE PROVIDE A COPY OF YOUR ORIGINAL SOFTSHOP SITE LICENCE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG8 | TI505 SOFTSHOP SITE LICENCE ONE YEAR UPGRADE LICENCE AGREEMENT INSIDE WARRANTY PERIOD FOR EIGHT LICENCE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:SSSS505-UPG9 | TI505 SOFTSHOP SITE LICENCE ONE YEAR UPGRADE LICENCE AGREEMENT OUTSIDE WARRANTY PERIOD FOR EIGHT LICE | ST44 | MTO | Unit | 89 | 0 | 100% | 0
PPX:TBU-STI-10S | TI505 INJECTION MOULDING PACKAGE | ST44 | 10 | Unit | 89 | 0 | 100% | 0